## Slide 1: Showcasing the PROFINET Suitcase with TIA Philipp Jauch (PMM Industrial Communications) Amjad Badar (Lead FAE)

## Slide 2: PROFINET Architecture (Three Main Components)
IO Supervisor
Engineering Tool
IO Controller (PLC)
IO Device
PROFINET Cyclic
Data exchange
Configuration
Configuration

## Slide 3: PROFINET Enabled Managed Switch in Profinet Network
IO Supervisor
IO Controller (PLC)
IO Device
IO Device
SDS-G3000
IO Device
Data Consumer
Data Producer
Notes: IO Device: Data Producer
IO Controller: Data Consumer
IO Supervisor: Device Configuration

## Slide 4: Integration of PROFINET Switches In TIA Portal
1st Use-Case PROFINET CC:B Basic Integration
  How to setup EDS-4000
  Using PN-IO data in PLC
2nd Use-Case PROFINET CC:B Shopfloor Security
  Example Application “Intruder Alert”
  Use Switch Port Data
  Message PLC/HMI/SCADA about suspicious connections

## Slide 5: Integration of PROFINET Switches In TIA Portal

## Slide 6: Integration of PROFINET Switches In TIA Portal
represent by
Download
Configuration
IO Controller (PLC)
Import
Engineering Device
SDS-G3000
IO Device
Example Switch Port Status

## Slide 7: Supporting Material
Supported products:
  EDS-4000 Series Managed Ethernet Switches
  EDS-G4000 Series Managed Ethernet Switches
  MDS-G4000 Series Managed Ethernet Switches
  MDS-G4000-L3 Series Managed Ethernet Switches
  MDS-G4000-4XGS Series Managed Ethernet Switches
  MDS-G4000-L3-4XGS Series Managed Ethernet Switches
  RKS-G4000 Series Managed Ethernet Switches
Pages 245-247
Pages 274-287
Link to Manual:
https://cdn-cms-frontdoor-dfc8ebanh6bkb3hs.a02.azurefd.net/getmedia/1f668af3-306f-421a-888a-71dc562d23e4/moxa-managed-switch-next-generation-os-v4.x-layer-2-user-manual-manual-v1.3.pdf

## Slide 8: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch

## Slide 9: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch

## Slide 10: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Go to Product Page on Moxa Homepage

## Slide 11: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Go to Resources and download GSD File

## Slide 12: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Go to WebGUI on switch and enable PROFINET

## Slide 13: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Confirm Notification

## Slide 14: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Copy BMP and GSDML into TIA Portal Project GSD Folder

## Slide 15: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Import GSD into TIA Portal

## Slide 16: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Select according GSD file for Moxa Switch and install

## Slide 17: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Confirm Import Success

## Slide 18: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Choose Moxa Switch from HW catalog at Network View

## Slide 19: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Select and drop switch into main field

## Slide 20: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Assign Switch to PROFINET Controller (likely main PLC)

## Slide 21: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
Below at the Properties and Ethernet addresses define IP address and set PROFINET name (either by system or manually)
PROFINET name is generated but it has to manually configured in the switch

## Slide 22: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 To receive cyclic data from PROFINET switch change to Device View; First add Cyclic Device Status; Select and drag to blue indicated field

## Slide 23: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Repeat for Cyclic Port Data

## Slide 24: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 You can now see and edit the range for the digital input area (I address)

## Slide 25: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Go to Properties and IO Tags to name the ports accordingly

## Slide 26: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
 Copy PROFINET Name of Switch and download project to PLC

## Slide 27: 1st Use-Case PROFINET CC:B Basic Integration
Wire devices
Download GSD file
Activate PN functionality in switch
Import GSD file in TIA Portal
Add device and port info
Set PN name for switch
Open your browser and access the IP address of your switch; Go to Industrial Application PROFINET and insert PROFINET name of TIA project; Apply

## Slide 28: 2nd Use-Case PROFINET CC:B Shopfloor Security
  Program Explanation:
  Ports which are in use are monitored in program and can be either logged in system or be put on HMI/SCADA to notify OT shopfloor if connections are down
  Unused ports can be monitored and OT shopfloor can be notified on HMI/SCADA if connections occur

## Slide 29: 2nd Use-Case PROFINET CC:B Shopfloor Security
  Program Explanation:
  Ports which are in use are monitored in program and can be either logged in system or be put on HMI/SCADA to notify OT shopfloor if connections are down
  Unused ports can be monitored and OT shopfloor can be notified on HMI/SCADA if connections occur
You can use the port info like any other digital input.
In this example we have assigned the port info to an LED on the control cabinet to show port status for OT shopfloor.
It can easily be shown in HMI or SCADA

## Slide 30: 2nd Use-Case PROFINET CC:B Shopfloor Security
  Program Explanation:
  Ports which are in use are monitored in program and can be either logged in system or be put on HMI/SCADA to notify OT shopfloor if connections are down
  Unused ports can be monitored and OT shopfloor can be notified on HMI/SCADA if connections occur
If you have ports which should stay unconnected, you can put all digital inputs of these ports on a SR (Set/Reset).
When somebody connects on these ports the Output changes to 1 and stays like this even if the “intruder” disconnects again.
This way OT shopfloor can check machine status and acknowledge the notification when machine status is okay.
Think about adding it to logs to capture date and time.