## Slide 1: MGate MB3x70-G2 Proprietary Serial Protocol Hands-On Introduction

## Slide 2: Hands-On - Introduction
Customers Requirement - Proprietary Serial Protocol
Integrating a Continuous RS-232 ASCII data stream from an LKW/PKW Scale with Moxa MGate MB3x70-G2
In this exercise, you will integrate a continuously streaming RS-232 ASCII weight data stream from a scale (LKW Waage) into an industrial network using the Moxa MGate MB3x70-G2 Series and its Proprietary Serial Protocol feature.
Truck scales commonly transmit a fixed ASCII frame at a defined interval (e.g., 1 Hz or 5 Hz). Your task is to configure the MGate to:
Detect frame boundaries
Parse weight (kg)
Extract status
Map structured data into Modbus registers
This simulates a real modernization scenario: converting legacy serial ASCII output into structured industrial data without changing the scale hardware.

## Slide 3: Hands-On - Introduction
Technical Scenario
Serial Input (RS-232 115200 8n1)
MGate Operation Mode: Consumer (Continuous data stream)
Transmission rate: 1 frame per second
Format: Fixed ASCII frame
Example frame structure:
<STX><SIGN><WEIGHT><UNIT><SPACE><STATUS><CR><LF>
Field | Example | Description
STX | 0x02 | Start of text
SIGN | '+' | '+' or '-'
WEIGHT | 012345 | 6 ASCII digits (kg)
UNIT | KG | ASCII “K” “G”
SPACE | 0x20 | Separator
STATUS | G | G = Gross (stable)
CR LF | 0D 0A | Frame termination

## Slide 4: Hands-On - Introduction
Example Frame (ASCII)
Example weight: 12345 kg (positive, gross, stable)
<STX>+012345KG G<CR><LF>
ASCII representation:
+012345KG G
Hex Representation (Raw Serial Input)
Below is the exact byte sequence you can inject into a serial port once per second:
02 2B 30 31 32 33 34 35 4B 47 20 47 0D 0A
Used in Simulation tool, Copy & Paste to PComm (see Appendix C)

## Slide 5: Hands-On - Introduction
Byte Breakdown
Byte | Hex | Meaning
1 | 02 | STX
2 | 2B | '+'
3 | 30 | '0'
4 | 31 | '1'
5 | 32 | '2'
6 | 33 | '3'
7 | 34 | '4'
8 | 35 | '5'
9 | 4B | 'K'
10 | 47 | 'G'
11 | 20 | Space
12 | 47 | 'G' (Gross/Stable)
13 | 0D | Carriage Return
14 | 0A | Line Feed

## Slide 6: Hands-On - Introduction
Integration Target (MGate MB3000-G2)
You need to configure:
  Frame detection starting at 0x02 (Start Delimiter)
  Extract bytes 1–7 as weight with sign (Data, ASCII → integer 32bit)
  Extract byte 8-9 (Unit, Constant)
  Extract byte 10 (Space, Constant)
  Extract byte 11 (Status, Constant)
  Frame termination at 0x0D 0x0A (End Delimiter)
  Map values into Modbus registers (Tags as Input Register)

## Slide 7: Hands-On - Introduction
MGate MB3270-G2
LAN x: 192.168.127.200/24
Proprietary Serial/RS-232 (Consumer)
Simplified Topology
Modbus TCP (Client / Master)
192.168.127.100/24
PC 1: raMBu2
Proprietary Serial
(Producer)
192.168.127.100/24
PComm using Serial COM Port
UPort USB to Serial Adapter
Ethernet
Serial
  PC (Laptop) IP out of the 192.168.127.0 network, not conflicting with MGate IP
  MGate default IP address is 192.168.127.254
  MGate IP address adjustment rule 192.168.127.[100 + <table nb.> + <team nb.>]
    Example: If table number is 20, team 2  last octet is 100 + 20 + 2 = 122  IP = 192.168.127.122

## Slide 8: Hands-On - Introduction
MGate MB3270-G2
Modbus TCP (Client / Master)
192.168.128.100/24
LAN1: 192.168.127.200/24
ID1, 9600, 8, n, 1
Modbus Server (Slave)
(XY- MD02 Sensor)
Modbus TCP
Proprietary Serial/RS-232 (Consume)
Serial interface: Port 1
PC 2: raMBu2
Full Topology
Modbus TCP (Client / Master)
192.168.127.100/24
PC 1: raMBu2
Modbus TCP
LAN2: 192.168.128.200/24
Proprietary Serial
(Produce)
192.168.x.100/24
PC 1 or 2: PComm
Modbus RTU/RS-485

## Slide 9: Hands-On - Introduction
Hardware & Software Prerequisites
1 x 24 VDC Power Supply (For device power, see also QIG for information how to power up the device)
1 x MGate-MB3250–G2
1 x UPort 1150
1 x RS232 Serial Cable
1 x PC with:
  PC Administration Rights required (IP change needed)
  Native Ethernet Port (LAN connective required)
  Software preinstall
    Device Search Utility v3.x
    UPort Driver
    PComm Terminal emulator

## Slide 10: Hands-On - Introduction
Hands-On workflow
Part 1 (~ 15 min*)
  Configure Custom Protocol conversion
Part 2 (~ 10 min*)
  Monitor serial traffic with build-in tools
  Add Modbus Tags for weight value
* Estimated time to be used for the module to be completed. If you reach ~80% of the time, ask your Table Coach for help if needed

## Slide 11: Questions?

## Slide 12: Hands-On

## Slide 13: Hands-On – Part 1
Configure Customer Protocol conversion
Task 1
  Setup your test environment
    Use Simplified Topology or Full Topology setup.
    Connect to MGate via Ethernet and login to Web UI
    Connect UPort to PC (see Appendix A)
    Use PComm Terminal Emulator to send Serial Data Stream (see Appendix B & C)
Task 2
  Configure Custom Serial Frame
    Select operation mode
    Add Frame
~ 15 min
See next Slides for some Hints

## Slide 14: Hands-On – Part 1
Configure Customer Protocol conversion

## Slide 15: Hands-On – Part 1
Configure Customer Protocol conversion

## Slide 16: Hands-On – Part 1
Frame setup (1 of 3)
Add Data and Constand Block
See next Slide for details

## Slide 17: Hands-On – Part 1
Frame setup (2 of 3)
Frame view after setup

## Slide 18: Hands-On – Part 1
Frame setup (3 of 3)
Do not Forget to Click Apply

## Slide 19: Hands-On – Part 2
Monitor serial traffic with build-in tools
Check if Serial data are received
  Use Serial Protocol Monitor
  RX counter shall …
Check if Serial data are as expected
  Use Traffic Monitor
  Data stream as send by PComm shall …
Check if Tag Values are decoded
  Use Protocol Diagnostic
  Data Value is converted …
Check if Modbus TCP client can read data
  Add/Map Tag Value to Modbus Server as Modbus Input Register
  Use Modbus TCP client simulation tool (e.g.: raMBu2)
  Configured Modbus Register contain …
~ 10 min

## Slide 20: Hands-On – Part 2
Monitor - Check if Serial data are received – Serial Port Monitor
If no serial data indication
  Check Serial Port type
    Right RSxxx type selected
  Check cable wiring
    Null modem used?
    Right pins connected?
  Check Serial Parameter
    Baud rate …
If error counter increase
  Check cable wiring
  Check Serial Parameter

## Slide 21: Hands-On – Part 2
Monitor - Check if Serial data are as expected – Traffic Monitor
If no serial data indication
  Validate Serial Port Monitor
If Frame size or Data unexpected
  Check Frame setup
  Check Sending device

## Slide 22: Hands-On – Part 2
Monitor - Check if Tag Values are decoded – Protocol Diagnostic
If Tag View value unexpected
  Validate Frame setup
If Status not Normal
  Check Sending device

## Slide 23: Hands-On – Part 2
Add Modbus Slave Tags

## Slide 24: Hands-On – Part 2
Add Modbus Slave Tags
Do not Forget to Click Apply

## Slide 25: Hands-On – Part 2
Validate function with Modbus TCP client (raMBu)
Configure Modbus TCP Client (raMBu) to connect to MGate MB3x70-G2 Server
Select Target Configuration
Adjust Target IP

## Slide 26: Hands-On – Part 2
Validate function with Modbus TCP client (raMBu)
Configure Modbus Register Read options
Select Target IP
Set Modbus Read Function
Set Register address & quantity
Set Sapping & Unit Type
Start Cyclic Read
Make sure Device ID match with your MGate Modbus TCP Server (Server ID) configuration

## Slide 27: Hands-On – Part 2
Validate function with Modbus TCP client (raMBu)
Validate Modbus Read value
Select Response Decoded
Validate Value

## Slide 28: Questions?

## Slide 30: Appendix A
UPort 1150 Interface configuration.
If not already installed, install UPort Driver found on:
UPort 1100 Series Product Page
Open Windows Device Manager as Administrator
Locate “Mulit-port serial adapters” and select/open the UPort 1150 properties
Move to “Port Configuration” tab and adjust the Interface mode according the Hands-On needs. (RS232, or RS485 2W or RS485 4W)

## Slide 31: Appendix B
How to use PComm as Serial Terminal emulator
First, identify the COM port number associated with UPort by using
Windows Device Manager
Second, open COM port (Serial Terminal) in PComm as shown below.

## Slide 32: Appendix C
PComm send Pattern configuration
022B3031323334354B4720470D0A
Pattern To be send from Terminal as
Data Stream
(copy & past below string to the HEX field)
Right click with Mouse into
the Terminal used for UPort
connection and select
“Send Pattern”
TX Counter shall start increasing