## Slide 1
March 2026
MGate MB3x70-G2 Introduction The Next Generation Modbus Protocol Gateway
Lubos Kucharek & Christian Gromeier
MTSC Troubleshooting 2026

## Slide 2: Agenda
Introduction (20 min.)
Hands On 1: Migration from G1 to G2 (60 min.)
Hands On 2: Expand & Integrate (30 min.)
Hands On 3: BONUS New Requirements (20 min.)
Debrief (10 min)

## Slide 3: Introduction

## Slide 4: Selecting the Proper Product Line
Beginning
After Upgrade
Problem?

## Slide 5: Product Highlights – MGate MB3170/3270/3470-G2
MGate MB3170/3270/3470-G2 Family
1, 2, 4-port Advanced Modbus Gateway
Certifications
Features and Benefits
Supports high-performing and low-latency Agent Mode to actively poll Modbus devices and cache data
Supports Modbus serial extensions or proprietary serial for various devices
Supports route by TCP port or IP address for different system architectures
Supports Modbus serial client to Modbus serial server communications
Ethernet cascading or dual subnet for flexible network system design
Web based traffic monitoring/diagnostic information for easy troubleshooting
Various models for different scenarios: serial port with 2 kV isolation (-I models), wide temperature range of -40 to 75°C (-T models), and fiber Ethernet models
Developed according to IEC 62443-4-2 with Secure Boot
UL, CE, FCC, DNV*, ATEX*, C1D2*, IECEx*
*Currently undergoing certification, with completion planned by the end of June 2026

## Slide 6: New Learning Content Industrial Connectivity Foundations
Soft Launch & Survey
Content Enrolment
Mandatory to complete
before 6th March 2026
Q2/2026
Overview of Industrial Connectivity (MTC-CON-100 | 18 min)
Ethernet Based IO Basics (MTC-CON-105 | 15 min)
Serial Communication Fundamentals (MTC-CON-110 | 20 min)
Basics of Serial to Ethernet Technology (MTC-CON-115 | 25 min)
Introduction to Industrial Automation Protocols (MTC-CON-120 | 15 min)
Protocol Translation with Gateways (MTC-CON-125 | 22 min)
Modbus Overview (MTC-CON-130 | 15 min)
7 Lectures & 7 Quizzes & Survey
Login https://moxa.litmos.com.au
Home > My Training > Not Started

## Slide 7
Configuration & Monitoring
  Web Console (No MGate Manager)
  Device Search Utility 3.1 (at least 3.X)
  raMBu2 Modbus TCP Client
  Moxa Windows Driver Manager v3.7/4.4 (Real COM, Proprietary Serial)
  PComm Lite 1.9 - Serial Communication Tool

## Slide 8: Hands-On Scenario

## Slide 9: Hands On´s Scenario: Car Wellness Center
A car, fixed on a conveyor
moves through the wash line.
Overengineering?
A truth “car wellness” in Germany!

## Slide 10: Hands-On 1 (60 min.)

## Slide 11: Hands-On 1: Migration From G1 to G2
Modbus TCP Application Client (Master)
Serial Sensor Modbus RTU Server (Slave)
Serial
Ethernet
After Migration
Modbus TCP Application Client (Master)
Serial Sensor Modbus RTU Server (Slave)
Serial
Ethernet
Beginning
Situation
- Car wash line used the MGate MB3270 (G1) for 10+ years
- Recently: communication instability reported
- Service technician confirmed sensors operational
- Issue not resolved during first visit
- Original configuration backup available
Decision
- Replace MGate MB3270 (G1) with MGate MB3270-G2
- Selected for future EU cybersecurity compliance
- Migration performed using latest backup
- Customer reports: “Migration successful – communication not working.”
Action plan
- Validate configuration integrity after migration
- Limited testing tools on site
- Use MGate´s built-in diagnostics + SCADA to find root cause

## Slide 12
https://www.moxa.com/en/products/industrial-edge-connectivity/protocol-gateways/modbus-tcp-gateways/mgate-mb3170-g2-mb3270-g2-mb3470-g2-series#resources
Migration G1 to G2

## Slide 13: Transparent mode
1
2
3
4
SCADA
Modbus TCP
Modbus RTU
Transparent Conversion
Ethernet
Serial
Available since
MGate MB3x70 Series “2nd Generation”
“On-the-fly” protocol translation
Modbus Client (Master)
Modbus Server (Slave)
G a t e w a y
Request
Response
Ethernet
Serial

## Slide 14: Trouble Shooting New Build-in Diagnostic Tools
One click diagnostic information log collection

## Slide 15: MGate´s Diagnostics

## Slide 16: Hands-On 2 (30 min.)

## Slide 17: Hands-On 2: Expand & Integrate
Situation
- Local system now operating correctly with MGate MB3270-G2
- Customer satisfied with migration result
- Chain management recently deployed a new central SCADA system
- Network segmentation between branches (located in different subnet)
- Request: Add remote monitoring to headquarters
- Preferably, no extra hardware
Challenges
1. Enable dual-subnet architecture using a single gateway
2. Prove that the same physical device can
Use the same, existing structure in current local branches
As well as address different addressing structure to
being integrated in the central system
Action plan
Reconfigure current setup for use in different subnets
Review capability of re-addressing current Modbus sensor

## Slide 18: Use in Different Subnets Dual IP LAN Mode
Flexible System Architecture
Modbus TCP devices can belong to different subnets by using dual IP in MGate
Modbus TCP
Modbus RTU/ASCII
Real COM
Modbus TCP
Modbus RTU/ASCII
Real COM
MGate
Client
Server
Can belong to different subnets

## Slide 19: Agent Mode for Better Performance
1
2
SCADA
Modbus TCP
Modbus RTU
Ethernet
Serial
A
B
Agent Mode
MGate will be an agent to collect data for you
MGate actively polls the device and caches the data
The SCADA gets data from MGate immediately
Available since
MGate MB3x70 Series – 2nd Generation
Active “polling” to refresh a Data Table
Modbus Client (Master)
Modbus Server (Slave)
G a t e w a y
Response
Ethernet
Serial
Request
Request
INTERNAL MEMORY
Response

## Slide 20: BONUS Hands-On 3

## Slide 21: Hands-On 3: Expand New Requirements
Situation
- Local system stable (temperature & humidity monitoring)
- Able to add to central management system
- Customer reports issue with heavily loaded vehicles
- Existing industrial vehicle scale available at entrance
Idea: measure vehicle weight before entering conveyor
Technical challenge
- Additional serial device (scale) to be integrated
- Different protocol / proprietary serial communication
- Maintain current temperature & humidity monitoring
- Ensure SCADA can read both:
- Environmental data
- Vehicle weight data
Action plan
- Identify scale interface, protocol, communication parameters
- Connect scale to available port and configure gateway interface
- Map weight data to SCADA
Potential to standardise all Branches Europe

## Slide 22: Proprietary Serial Device
Non-standard Modbus and Serial Proprietary to Modbus TCP conversion
  Supports Agent mode
  Simultaneously with standard Modbus RTU/ASCII Server
Supported Modes
  Request / Response = Time-Based (Scheduled/Periodic)
  Produce / Consume = Time-Independent (Continuous/Event-Based)
Modbus TCP
Client
Serial Proprietary Server
and / or
Data cached in MGate for active polling
New Supported Architecture
Modbus RTU/ASCII Server

## Slide 23: Proprietary Serial Settings Example Frame Format
Take the response of the Modbus RTU function code 03 as an example
The function block settings would be:
Function Code
Slave ID
Byte Count
Data
CRC
Supports 4 Function Blocks
  Node Address: Like Device ID
  Constant: A tag with a fixed length and an unchanging value
  Data: A tag with a fixed length but a variable value
  Checksum: Used for checksum calculation

## Slide 24: Customers Requirement - Proprietary Serial Protocol
Integrating a Continuous RS-232 ASCII data stream from an LKW/PKW Scale with Moxa MGate MB3x70-G2
In this exercise, you will integrate a continuously streaming RS-232 ASCII weight data stream from a scale (LKW Waage) into an industrial network using the Moxa MGate MB3x70-G2 Series and its Proprietary Serial Protocol feature.
Truck scales commonly transmit a fixed ASCII frame at a defined interval (e.g., 1 Hz or 5 Hz). Your task is to configure the MGate to:
Detect frame boundaries
Parse weight (kg)
Extract status
Map structured data into Modbus registers
This simulates a real modernization scenario: converting legacy serial ASCII output into structured industrial data without changing the scale hardware.

## Slide 25: Proprietary Serial Protocol
Technical Scenario
Serial Input (RS-232 115200 8n1)
MGate Operation Mode: Consumer (Continuous data stream)
Transmission rate: 1 frame per second
Format: Fixed ASCII frame
Example frame structure:
<STX><SIGN><WEIGHT><UNIT><SPACE><STATUS><CR><LF>
Field | Example | Description
STX | 0x02 | Start of text
SIGN | '+' | '+' or '-'
WEIGHT | 012345 | 6 ASCII digits (kg)
UNIT | KG | ASCII “K” “G”
SPACE | 0x20 | Separator
STATUS | G | G = Gross (stable)
CR LF | 0D 0A | Frame termination

## Slide 26: Proprietary Serial Protocol
Example Frame (ASCII)
Example weight: 12345 kg (positive, gross, stable)
<STX>+012345KG G<CR><LF>
ASCII representation:
+012345KG G
Hex Representation (Raw Serial Input)
Below is the exact byte sequence you can inject into a serial port once per second:
02 2B 30 31 32 33 34 35 4B 47 20 47 0D 0A

## Slide 27: Proprietary Serial Protocol
Integration Target (MGate MB3000-G2)
You need to configure:
  Frame detection starting at 0x02 (Start Delimiter)
  Extract bytes 1–7 as weight with sign (Data, ASCII → integer 32bit)
  Extract byte 8-9 (Unit, Constant)
  Extract byte 10 (Space, Constant)
  Extract byte 11 (Status, Constant)
  Frame termination at 0x0D 0x0A (End Delimiter)
  Map values into Modbus registers (Tags as Input Register)
Use PowerPoint File included in the Session directory
  MGate-MB3x70-G2_HandsOn3_ProprietarySerialProtocol_v1a.pptx

## Slide 28
Thank you for your attention
and good luck!

## Slide 29: Hands-On 1 Instructions

## Slide 30: Hands-On 1: Migration From G1 to G2
Modbus TCP Application Client (Master)
Serial Sensor Modbus RTU Server (Slave)
Serial
Ethernet
After Migration
Modbus TCP Application Client (Master)
Serial Sensor Modbus RTU Server (Slave)
Serial
Ethernet
Beginning
Situation
- Car wash line used the MGate MB3270 (G1) for 10+ years
- Recently: communication instability reported
- Service technician confirmed sensors operational
- Issue not resolved during first visit
- Original configuration backup available
Decision
- Replace MGate MB3270 (G1) with MGate MB3270-G2
- Selected for future EU cybersecurity compliance
- Migration performed using latest backup
- Customer reports: “Migration successful – communication not working.”
Action plan
- Validate configuration integrity after migration
- Limited testing tools on site
- Use MGate´s built-in diagnostics + SCADA to find root cause

## Slide 31: Hands-On 1 – Architecture
MGate MB3270-G2
Modbus TCP (Client / Master)
192.168.127.100/24
LAN1: 192.168.127.200/24
ID1, 9600, 8, n, 1
Modbus Server (slave)
(XY-MD02 Sensor)
Modbus TCP
Modbus RTU
Serial interface: Port 1
PC 1: raMBu2

## Slide 32
Hands-On 1.1
Each Table Group shall use the same IP address range, check out the IP Address according the session.
Power up and reset the MGate MB3270-G2 to the factory defaults
Verify your hands-on architecture, keep the serial sensor unplugged
Use DSU (Device search utility 3.1) to search and locate the MGate MB3270-G2
Review and if needed setup your PC network adapter settings
Reach out the MGate via web console

## Slide 33
Hands-On 1.1
Migrate the configuration from G1 to G2 (Use provided configuration file provided for MTSC 2026) - configuration backup´s account: “Admin” / password: “moxa”
- align IP address accordingly to scenario´s architecture
7. Login to device, review status LED, the dashboard, ensure the topology after migration

## Slide 34
Hands-On 1.2
Connect the sensor to the serial port, accordingly with topology, review Protocol Dashboard
Test via MGate´s Modbus Device feature whether the Modbus RTU Sensor is communicating properly
For proper Modbus´s command setup, find the Device ID, Function, Address, Quantity, in Sensor´s user manual, (configuration file provided for MTSC 2026)
If result is invalid, use MGate´s Diagnostics to find out if the serial port connection works as expected. - Are you receiving the serial data from sensor?
Validate the configuration and test the serial device, until completed as valid

## Slide 35
Hands-On 1.3
Start raMBu2 configure Target Interface for Modbus TCP Modbus. Then, connect to MGate
- Can you establish stable connection?
If not, use MGate´s Diagnostics to find out if there is any issue in Ethernet connection between MGate and Client.
Validate the configuration until you can establish a stable connection

## Slide 36
Hands-On 1.3
Setup Modbus Commands to query data from the sensor, via MGate
Device ID
Function
Address
Quantity
Can you read Temperature and Humidity? What diagnostic in the client says?
Review the Traffic via MGate to find out the root cause, if needed - enable Modbus TCP Exception and compare the diagnostics, is there any difference?
Validate the configuration of Modbus Protocol, until you can read the data

## Slide 37
Hands-On 1.3
What a temperature and humidity is measured by sensor? Interpret the data via Modbus TCP Client.
Validate the Temperature and Humidity via MGate´s Conversion Tool in Diagnostics
Validate Connection between raMBu and Sensor via MGate´s Protocol Diagnostics

## Slide 38: Hands-On 2 Instructions

## Slide 39: Hands-On 2: Expand & Integrate
Situation
- Local system now operating correctly with MGate MB3270-G2
- Customer satisfied with migration result
- Chain management recently deployed a new central SCADA system
- Network segmentation between branches (located in different subnet)
- Request: Add remote monitoring to headquarters
- Preferably, no extra hardware
Challenges
1. Enable dual-subnet architecture using a single gateway
2. Prove that the same physical device can
Use the same, existing structure in current local branches
As well as address different addressing structure to
being integrated in the central system
Action plan
Reconfigure current setup for use in different subnets
Review capability of re-addressing current Modbus sensor

## Slide 40: Hands-On 2 – Architecture
MGate MB3270-G2
Modbus TCP (Client / Master)
192.168.128.100/24
LAN1: 192.168.127.200/24
Modbus Server (Slave)
(XY- MD02 Sensor)
Modbus TCP
Serial interface: Port 1
PC 2: raMBu2
Modbus TCP (Client / Master)
192.168.127.100/24
PC 1: raMBu2
Modbus TCP
LAN2: 192.168.128.200/24
Modbus RTU/RS-485
ID1, 9600, 8, n, 1
Sensor ID: 10
Temperature Address: 11
Humidity Address: 12

## Slide 41
Hands-On 2.1
Continue after previous hands on 1.3 - in case, you did not complete the previous hands on 1.3 - import a configuration backup “MG-MB3270_Solution_1_3” and restart device - configuration backup´s account: “Admin” / password: “moxa1234”
Verify your hands-on architecture, keep the serial sensor plugged
Decide with partner who is going to act as Remote SCADA and setup the PC2 network adapter settings
Review Networks Settings in MGate, accordingly with topology for 2.1 Hands-on
Run and configure setup for Modbus TCP Client at PC2 and query for temperature and humidity values
Connect and query temperature and humidity values simultaneously also with PC1
Interpret the values and validate connections from both Modbus TCP Clients, via MGate

## Slide 42
Hands-On 2.2
The customer has provided information about expected structure (architecture, Hands-On 2): - the remote SCADA system can implement the sensor under ID 10 - the temperature´s register needs to be assigned to address 11 - the humidity´s register needs to be assigned to address 12
Review and evaluate whether is needed to change operation mode of MGate
Is this achievable with MGate in Transparent mode? Is it possible to use current configuration? Why?

## Slide 43
Hands-On 2.2
Import a configuration backup “MG-MB3270_HandsOn_2_2” and restart device - configuration backup´s account: “Admin” / password: “moxa1234”
Review Current operation mode of MGate, after the configuration import
Can you read temperature and Humidity values data from both Modbus TCP Clients (PC1, PC2)?

## Slide 44
Hands-On 2.2
Setup TCP Server role in MGate, accordingly with new structure, provided from customer - ID, Register addresses.. Review architecture, Hands-On 2
Align Setup to query temperature and Humidity via Modbus TCP Client, on PC2 only - keep original setup on PC1 - architecture, Hands-On 2
Can Modbus TCP Client query temperature and humidity from PC2? Interpret the values
Can Modbus TCP Client query temperature and humidity from PC1?
Align Setup to query temperature and humidity via Modbus TCP Client, on PC1 too
Can Modbus TCP Client query temperature and humidity from PC1? Interpret the values
Validate expected connection via MGate
Can you read temperature and Humidity values data from both Modbus TCP Clients (PC1, PC2)?

## Slide 45: BONUS Hands-On 3 Instructions

## Slide 46: Hands On 3: New Requirements
Situation
- Local system stable (temperature & humidity monitoring)
- Able to add to central management system
- Customer reports issue with heavily loaded vehicles
- Existing industrial vehicle scale available at entrance
Idea: measure vehicle weight before entering conveyor
Technical challenge
- Additional serial device (scale) to be integrated
- Different protocol / proprietary serial communication
- Maintain current temperature & humidity monitoring
- Ensure SCADA can read both:
- Environmental data
- Vehicle weight data
Action plan
- Identify scale interface, protocol, communication parameters
- Connect scale to available port and configure gateway interface
- Map weight data to SCADA
Potential to standardise 1000+ Branches Europe
See next Slide for details

## Slide 47: Proprietary Serial Protocol
Integration Target (MGate MB3000-G2)
You need to configure:
  Frame detection starting at 0x02 (Start Delimiter)
  Extract bytes 1–7 as weight with sign (Data, ASCII → integer 32bit)
  Extract byte 8-9 (Unit, Constant)
  Extract byte 10 (Space, Constant)
  Extract byte 11 (Status, Constant)
  Frame termination at 0x0D 0x0A (End Delimiter)
  Map values into Modbus registers (Tags as Input Register)
Use PowerPoint File included in the Session directory
  MGate-MB3x70-G2_HandsOn3_ProprietarySerialProtocol_v1a.pptx

## Slide 48: Appendix A

## Slide 49: Modbus Protocol & Key Benefits
Developed by Modicon, 1979
Transparency, Simplicity & Reliability
  Open standard protocol
  Standardized register access, Request / Response mechanism
  Built-in Exception Codes
REQUEST [Slave Address] [Function Code] [Data...]
NORMAL RESPONSE: [Slave Address] [Function Code] [Data...]
EXCEPTION RESPONSE [Slave Address] [Function Code + 0x80] [Exception Code]
Modbus Client (Master)
Modbus Server (Slave)

## Slide 50: Data Organization Overview

## Slide 51: Modbus Types
Modbus RTU/ASCII
  Serial communication
  Single master, multiple slaves
  Small, localized network
Modbus TCP
  Ethernet (TCP/IP)
  Multiple clients and multiple servers
  Larger, distributed networks

## Slide 52: Modbus RTU
One Single Client (Master)
Multiple Slave Devices (Based Serial Interface)
  RS-232: 1-to-1 (up to 15m)
  RS-422: 1-to-1 (up to 1200m)
  RS-485: 1-to-31 (up to 1200m)
Each Server (Slave) > Unique ID
More Connected Devices > Longer polling cycles
ID:1
ID:2
RS-485 2-Wire

## Slide 53: Modbus TCP/IP
Multiple Masters/Clients
Higher Communication Speed
Easy Integration
Scalability and Flexibility
Modbus TCP Server
Modbus TCP Client
Modbus TCP Client
Modbus on RS232
Modbus on RS485
Modbus on RS485
Modbus TCP Client
Modbus TCP Server
Modbus TCP Server
Modbus TCP Server

## Slide 54: Message Frame TCP vs. RTU
by: ipc2u.com
PDU (Protocol Data Unit)
  Removing Slave ID & CRC
MBAP header (Modbus App. Header)
  Transaction ID – 2 bytes
  Protocol ID – 2 bytes
  Length – 2 bytes
  Unit ID – 1 byte
MBAP + PDU
  Modbus TCP/IP ADU